## Intro
This workbook calculates manually some of the formulae from the ASHRAE Handbook - Fundamentals, ch. 1, for comparison with
values calculated by PsychroLib.
Didier Thevenard - Nov 2018

## SI
Manual calculation of some of the formulae in psychrolib
Calculation of humidity ratio from vapour pressure (eq. 20 in H-F)
| VapPres (Pa) | Pressure (Pa) |  |  | Humidity ratio
| 3169.7 | 95461 |  |  | 0.02136
Calculation of humidity ratio from wet bulb temperature (eq. 33 & 35 in H-F)
Above freezing
| TDryBulb (C) | TWetBulb (C) | Pressure (Pa) | SatVapPres (Pa) | Wsstar | HumRatio
| 30 | 25 | 95461 | 3169.7 | 0.02136 | 0.019228
Below freezing
| TDryBulb (C) | TWetBulb (C) | Pressure (Pa) | SatVapPres (Pa) | Wsstar | HumRatio
| -1 | -5 | 95461 | 401.74 | 0.0026285 | 0.001204
Calculation of moist air enthalpy, volume and density (eq. 30, 26 & 11 in H-F)
| TDryBulb (C) | HumRatio | Pressure (Pa) |  | MoistAirEnthalpy | MoistAirVolume | MoistAirDensity
| 30 | 0.02 | 95461 |  | 81316 | 0.94086 | 1.0841

## IP
Manual calculation of some of the formulae in psychrolib
Calculation of humidity ratio from vapour pressure (eq. 20 in H-F)
| VapPres (psi) | Pressure (psi) |  |  | HumRatio
| 0.45973 | 14.175 |  |  | 0.020847
Calculation of humidity ratio from wet bulb temperature (eq. 33 & 35 in H-F)
Above freezing
| TDryBulb (F) | TWetBulb (F) | Pressure (psi) | SatVapPres (psi) | Wsstar | HumRatio
| 86 | 77 | 14.175 | 0.45973 | 0.020847 | 0.018719
Below freezing
| TDryBulb (F) | TWetBulb (F) | Pressure (psi) | SatVapPres (psi) | Wsstar | HumRatio
| 30.2 | 23 | 14.175 | 0.058268 | 0.0025671 | 0.0011466
Calculation of moist air enthalpy, volume and density (eq. 30, 26 & 11 in H-F)
| TDryBulb (F) | HumRatio | Pressure (psi) |  | MoistAirEnthalpy | MoistAirVolume | MoistAirDensity
| 86 | 0.02 | 14.175 |  | 42.6168 | 14.7206 | 0.069291